Date: 13 May 2011

Part No.: PS80705

Fire Resistant Speaker Cables

Application                                        Preferably used for installation into conduit and surface wiring which provide flame retardant, low smoke & corrosive gases properties and maintain circuit integrity in case of fire.

Construction

Conductor: Class 2 stranded tinned copper wire

Insulation: Cross-linked polyethylene (XLPE)

Twisting: Two insulated conductors uniformly twisted together to form a pair.

Pair Identification: 1) Black/Blue; 2) Black/Green;

3) Blue/Green; 4) Black/Brown;

5) Blue/Brown; 6) Green/Brown

7) Black/White; 8) Blue/White

9) Green/White; 10) Brown/White

Overall Collective Screen: Aluminum/polyester tape applied with the metallic side down in electrical contact with a 0.5mm² tinned copper drain wire. A 23 micron isolation tape is applied over the screening tape with a minimum 50% overlap.

Jacket: Low smoke & halogen free compound (LSZH)

Jacket Color: Black

Packing: Delivered on non-returnable wooden drums.

Physical Characteristics

Voltage Rating: 300/500V

Temperature Rating: During Operation: -40°C to +90°C

During Installation: 0°C to +50°C

Minimum Bending Radius: 6 x overall diameter

Fire Performance

Flame Retardant: IEC 60332 part 1 and part 3

Fire Resistant: IEC60331, BS6387 CWZ

Low Smoke Emission: IEC 61034

Zero Halogen Gas Emission: IEC 60754

Oxygen Index: ≥35%

Technical Data

| No. of Pair | Size of Conductor | Conductor Stranding | Insulation Thickness | Sheath Thickness | Overall Diameter |
| --- | --- | --- | --- | --- | --- |
| No. | mm2 | No./mm | mm | mm | mm |
| 2 | 1.00 | 32/0.20 | 0.60 | 0.80 | 11.00 |
| 2 | 2.50 | 50/0.25 | 0.80 | 1.10 | 17.00 |
| 2 | 4.00 | 56/0.30 | 0.80 | 1.20 | 19.00 |
| 10 | 2.50 | 50/0.25 | 0.80 | 1.50 | 34.00 |
| 10 | 4.00 | 56/0.30 | 0.80 | 1.80 | 39.50 |

The data included in the present catalogue are merely indicative; Caledonian Cables Limited reserves to itself the right to change them as its own discretion in any time.

# Text boxes

XLPE Insulation

Mica Tape Fire Barrier

Tinned Copper Wire Conductor

Tinned Copper Drain Wire

Overall Aluminum Screen

LSZH Outer Jacket