Date: 29 July 2026

Part No.: PX79257

| Flame Retardant RG6 Coaxial Cable | 1.02mm BC / 4.58mmFPE/ Cu braiding/ FR LSZH |
| --- | --- |

Cable Specification

1.02mm BC, 4.58mmFoamed PE , 96*0.12mm Cu Braiding , 6.82mm FR LSZH

Construction

Conductor: 	 	       	18AWG annealed copper

Insulation:  	   				Foamed PE

Insulation Dia.:  				4.58mm ±0.20mm

Thickness:      				1.78mm

Braid:          				Cu braid,16/6/0.12mm

Jacket:		      				LSZH, flame retardant , anti-termite and anti-rodent

Thickness:       				0.80mm

Overall Diameter: 				6.82mm±0.20mm

Physical Properties

Temperature Rating:   		90 ℃

Approx.weight:         		56kg/km

Min.bending radius:     		15*Overall Diameter

Electrical Performance

Voltage rating					30V

Capacitance:          		54+/-2 pF/m

Impendence:			 		75 +/-3 Ohm

Conductor resistance at20℃:  21.8 Ω/km

Velocity of Propagation: 		83+/-1%

Screening Attenuation:  		≥85dB

Insulation resistance at 20 ℃: 	>5000 Mohm/km

Attenuation

| Frequency (MHz) | Attenuation ≤ (dB/100m) |
| --- | --- |
| 50 | 5.20 |
| 100 | 7.10 |
| 200 | 9.90 |
| 400 | 13.19 |
| 800 | 19.02 |
| 860 | 19.57 |
| 1000 | 21.45 |
| 1350 | 23.65 |
| 1750 | 27.10 |
| 2150 | 29.90 |
| 2400 | 31.70 |

Part No.:PC79353

| Flame Retardant Twisted Pair Cable Comply to:IEC60332-3 | 1×2×1.0mm2 /2×2×22AWG Cu/ LSZH/ OS/ FR LSZH |
| --- | --- |

Application:

These cables are specially designed for requirements concerning the smoke density and acidic gas emitted in case of fire. FIRETOX Cables are made with well chosen materials that not only can fulfill the conventional requirements of Low Smoke Halogen Free, but also can reduce flame propagation in those instance where fire may develop.

Construction:

Conductor:       	Stranded annealed copper/tinned copper wires to BS 6360, class 2

Insulation:         Low smoke,zero halogen (LSZH) insulated

Nominal thickness:	0.4-0.5 mm

Twisting:	Two colored insulated conductors are uniformly twisted together to form a pair.

Screen:          		Overall Aluminium/Polyester tape applied with the metallic side down in electrical contact with a 0.5 mm2 tinned copper drain wire(7*0.31mm formation).

A 23 micron polyester tape is applied over the screening tape with a minimum 50% overlap.

Sheathing:           	Flame retardant LSZH with anti-termite and anti-rodent additive

Nominal thickness: 0.7mm

Overall diameter:	1×2×1.0 mm2: 6.3+/-0.2mm,  2×2×0.35mm2: 6.86+/-0.2mm,

Packing:         		The cables are delivered on non-returnable wooden drums.

Standard            	IEC 60332-3

Physical characteristics:

Temperature rating:	  	-40 to +90℃

Minimum bending radius

-for fixed wiring: 20mm

Flame retardant:		IEC60332-3

Water resistant:     	IEC60529

Fire Retardancy Characteristics (For LSZH sheath):

Flame Propagation:	 IEC 332-1

Corrosive and Acid Gas Emission Test:	Hydrochloric acid yield less than 0.5% in accordance with IEC 60754-1&2

Smoke Density:    Percentage of light transmitted is greater than 60% when tested in

accordance  with  IEC 61034-1&2

Flammability: 	Temperature Index is around 250-280 deg when tested according to ISO 4589  or BS  2782 Part 1 Method 143A & 143

Electrical characteristics:

Rated voltage :                  		 300/500V

Max conductor resistance at 20℃ :

- for 1×2×1.0mm2:	 ≤18.2 Ohm/Km

- for 2×2×22AWG: 	 ≤48.4 Ohm/Km

Min insulation resistance :             ≥100 M ohm/Km

Test voltage:                         1000V

Part No.:PC79346

| Flame Retardant Multi-core Instrument Cable Comply to:IEC60332-3 | 6C×20AWG TC/ LSZH/ Wrapping/ OS/ FR LSZH |
| --- | --- |

Application:

These cables are specially designed for requirements concerning the smoke density and acidic gas emitted in case of fire. FIRETOX Cables are made with well chosen materials that not only can fulfill the conventional requirements of Low Smoke Halogen Free, but also can reduce flame propagation in those instance where fire may develop.

Construction:

Conductor:       	Stranded annealed tinned copper wires to BS 6360, class 2

Insulation:         Low smoke,zero halogen (LSZH) insulated

Nominal thickness:	0.4 mm

Wrapping:	Polyester tape

Screen:          		Overall Aluminium/Polyester tape applied with the metallic side down in electrical contact with a 0.5 mm2 tinned copper drain wire(7*0.31mm formation).

A 23 micron polyester tape is applied over the screening tape with a minimum 50% overlap.

Sheathing:           	Flame retardant LSZH with anti-termite and anti-rodent additive

Nominal thickness: 0.7mm

Overall diameter:	6.59+/-0.2mm

Packing:         		The cables are delivered on non-returnable wooden drums.

Standard            	IEC 60332-3

Physical characteristics:

Temperature rating:	  	-40 to +90℃

Minimum bending radius

-for fixed wiring: 20mm

Flame retardant:		IEC60332-3

Water resistant:     	IEC60529

Fire Retardancy Characteristics (For LSZH sheath):

Flame Propagation:	 IEC 332-1

Corrosive and Acid Gas Emission Test:	Hydrochloric acid yield less than 0.5% in accordance with IEC 60754-1&2

Smoke Density:    Percentage of light transmitted is greater than 60% when tested in

accordance  with  IEC 61034-1&2

Flammability: 	Temperature Index is around 250-280 deg when tested according to ISO 4589  or BS  2782 Part 1 Method 143A & 143

Electrical characteristics:

Rated voltage :                  		300/500V

Max conductor resistance at 20℃ :    	≤33.8 Ohm/Km

Min insulation resistance :            ≥100 M ohm/Km

Max inductance / resistance (L/R) ratio:	25 uH/ Ohm

Max. mutual capacitance at 1KHz:     120 pF/m

Capacitance unbalance at 1khz:      	250 pF/ 250m

Test voltage:

- core :core                     1000V

- core: screen                   1000V