Date: 24 Aug. 2011

Spec. No.: PP80221

Fire Resistant Instrumentation Cable

Application

These cables are fire resistant, flame retardant, low smoke, halogen free and oil resistant, used for instrumentation, communication, control and alarm systems.

Standard

BS6883

IEC 60092    IEC60331-21

Construction

Conductor:   			Stranded Copper Conductor to BS6360

Insulation:  			Mica tape+EPR Complying with BS7655 GP4

Nominal Thickness: 	0.6mm

Overall screen:  	Aluminium/ p.e.t.p. Laminated tape applied with the metallic side down in electrical contact with 20 AWG, 0.5mmsq tinned copper drain wire.

Bedding:   	EVA

Nominal Thickness: 	1.1mm

Armor:    			Galvanised Steel Wire Braid

Sheathing:   			EVA

Nominal Thickness: 	1.2mm

Sheath Color: 	 	Green or upon request

Packing:         			The cables are delivered on non-returnable wooden drums.

Physical Properties

Temperature rating:	  -20 to +90℃

Minimum bending radius: 8 x Overall Diameter

Fire resistant: IEC60331

Flame retardant: IEC60332 -3

Dimensional Data

| Conductor | Number of Pairs | Approx Nominal Dia under Armour (mm) | Approx Nominal Overall Dia (mm) | Armour Wire Dia (mm) | Approx Weight (kg/km) |
| --- | --- | --- | --- | --- | --- |
| 1.5mmsq (7/0.53mm) | 1 | 10 | 13.5 | 0.3 | 245 |
| 1.0mmsq (7/0.43mm) | 2 | 12 | 16 | 0.3 | 260 |

Electrical Data

| Conductor Area size | 1.5 | 1 |
| --- | --- | --- |
| Rated voltage | 250V | 250V |
| Nom. Inductance | 40 μH/ohm | 25 μH/ohm |
| Nom. conductor resistance at 20 ℃ | ≤12.9 Ohm/Km | ≤18.2 Ohm/Km |
| Maximum Mutual capacitance | 85pF/ m | 75pF/ m |